## F2.2
Adani Power Ltd.
MYT Petition Formats - Generation
Form 2.2: Energy Charges for Thermal Generation
Adani Dahanu Thermal Power Station
Sr. No. | Particulars | Units | FY 2022-23 |  |  |  | FY 2023-24 |  |  |  | FY 2024-25 |  |  |  |  | Ensuing Years |  |  |  |  | Remarks
|  |  | MTR Order* | April-March (Normative) | April-March (Audited ) | Provisional True-Up requirement | MTR Order* | April-March (Normative) | April-March (Audited ) | Provisional True-Up requirement | MTR Order* | Apr-Aug (Prov. Actual with normative parameters) | Sept-Mar (Estimated) | April - March (Estimated) | Provisional True-Up requirement | FY 2025-26 | FY 2026-27 | FY 2027-28 | FY 2028-29 | FY 2029-30
|  |  | (a) | (b) | (c ) | (b)-(a) | (a) | (b) | (c ) | (b)-(a) | (g) | (h) | (i) | (j) = (h) + (i) | (k) = (j) - (g) | Projected | Projected | Projected | Projected | Projected
1 | Operational Parameters
1.1 | Total Capacity | MW | 500 | 500 | 500 |  | 500 | 500 | 500 |  | 500 | 500 | 500 | 500
1.2 | Target Availability for full recovery of AFC | % | 85 | 85 | 85 |  | 85 | 85 | 85 |  | 85 | 85 | 85 | 85
1.2.1 | In High Demand Season | %
| Peak Hours | % |  | 100 | 100 |  |  | 96.4555 | 96.4555
| Off-Peak Hours | % |  | 100 | 100 |  |  | 96.9167 | 96.9167
1.2.2 | In Low Demand Season | %
| Peak Hours | % |  | 94.0664 | 94.0664 |  |  | 89.9749 | 89.9749
| Off-Peak Hours | % |  | 94.1807 | 94.1807 |  |  | 88.9066 | 88.9066
1.3 | Actual/Projected Availability | % | 88.8615 | 95.8286 | 95.8286 | 6.9671 | 92.8962 | 91.0341 | 91.0341 | -1.8621 | 93.0137 | 90.02% | 88.21% | 88.97% | -92.124
1.4 | Target PLF for Incentive | % | 85 | 85 | 85 |  | 85 | 85 | 85 |  | 85
1.5 | Actual/Projected PLF | % | 77.5596 | 79.74% | 79.884 | -76.7622 | 92.8962 | 73.49% | 73.964 | -92.1613 | 93.0137 | 75.44% | 75% | 75.18% | -0.17829
1.6 | Scheduled Generation | MU | 3397.1103 |  |  |  | 4080 |  |  |  | 4074
1.7 | Actual/Projected Gross Generation | MU | 3397.1103 | 3492.6287 | 3498.915 | 95.5184 | 4080 | 3227.6096 | 3248.4747 | -852.3904 | 4074 | 1385.094 | 1908 | 3293.094 | -780.906
1.8 | Normative Auxiliary Energy Consumption | %
| Normative Auxiliary Energy Consumption (Excluding FGD) |  | 8.5 | 8.5 | 8.644 |  | 8.5 | 8.5 | 9.066 |  | 8.5 | 8.5 | 8.5 | 8.5
| Actual Auxiliary Energy Consumption (FGD) |  | 1.2 | 1.2 | 1.218 |  | 1.2 | 1.2 | 1.214 |  | 1.2 | 1.2 | 1.2 | 1.2
1.9 | Actual/Projected Auxiliary Energy Consumption | % | 9.7% | 9.7% | 9.862% |  | 9.7% | 9.7% | 10.28% |  | 9.7% | 9.7% | 9.7% | 9.7%
1.1 | Actual/Projected Auxiliary Energy Consumption | MU | 329.5197 | 338.785 | 345.067 | 9.2653 | 395.76 | 313.0781 | 333.9432 | -82.6819 | 395.178 | 134.3541 | 185.076 | 319.4301 | -75.7479
1.11 | Actual/Projected Net Generation | MU | 3067.5906 | 3153.8437 | 3153.8437 | 86.2531 | 3684.24 | 2914.5315 | 2914.5315 | -769.7085 | 3678.822 | 1250.7399 | 1722.924 | 2973.6639 | -705.1581
1.12 | Normative Gross Station Heat Rate | kcal/kWh | 2430 | 2430 | 2430 |  | 2430 | 2430 | 2430 |  | 2430 | 2430 | 2430 | 2430
1.13 | Actual/Projected Gross Station Heat Rate | kcal/kWh | 2430 | 2430 | 2265 |  | 2430 | 2430 | 2272 |  | 2430 | 2430 | 2430 | 2430
1.14 | Normative Secondary Fuel Oil Consumption | ml/kWh | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5
1.15 | Actual/Projected Secondary Fuel Oil Consumption | ml/kWh | 0.5 | 0.5 | 0.081 |  | 0.5 | 0.5 | 0.175 |  | 0.5 | 0.5 | 0.5 | 0.5
1.16 | Normative Transit Loss | % | 0.8% / 0.2% / 0.8% | 0.8% / 0.2% / 0.8% | 0.8% / 0.2% / 0.8% |  | 0.8% / 0.2% / 0.8% | 0.8%/ 0.2% / 0.8% | 0.8%/ 0.2% / 0.8% |  | 0.8% / 0.2% | 0.8% / 0.2% | 0.8% / 0.2% | 0.8% / 0.2%
1.17 | Actual/Projected Transit Loss | % |  | 1.048% / 0.809% / 0.847% | 1.048% / 0.809% / 0.847% |  |  | 0.540% / 0.115%/ 1.451% | 0.540% / 0.115%/ 1.451%
2 | Fuel Parameters (for each primary and secondary fuel)
2.1 | Calorific Value (As billed) | kcal/kg | 3791.3029 | 3869.4392 | 3869.4392 | 78.1363 | 3766.2216 | 3845.2924 | 3845.2924 | 79.0707 | 3746.9168 | 3743.3645 | 3687.7196 | 3708.966 | -37.9509
2.1.1 | Fuel 1 - Domestic Coal | kcal/kg | 3733.4184 | 3765.4308 | 3765.4308 | 32.0124 | 3746.9168 | 3702.9376 | 3702.9376 | -43.9792 | 3746.9168 | 3637.4628 | 3714 | 3637.4628 | -109.454
2.1.2 | Fuel 2 - Imported Coal | kcal/kg | 4271.2231 | 4414.6515 | 4414.6515 | 143.4284 | 4390.4098 | 4048 | 4048 | -342.4098 | 0 | 4491 | 4491 | 4491 | 4491
2.1.3 | Fuel 3 - Raw Coal |  | 3751.9836 | 3837.3384 | 3837.3384 | 85.3547 | 0 | 3934.6062 | 3934.6062 | 3934.6062 | 0 | 3754.4605 | 3669.8174 | 3698.4691 | 3698.4691
2.1.4 | Fuel 4 - Addnl. Raw coal
2.1.5 | LDO | kcal/kg | 10812.2347 | 10813.8187 | 10813.8187 | 1.584 | 10810.3333 | 10764.6911 | 10764.6911 | -45.6422 | 10810.3333 | 10704.6515 | 10690.3631 | 10696.3729 | -113.9605
2.2 | Calorific Value (As received) | kcal/kg | 3720.2908 | 3740.156 | 3633.5118 | 19.8652 | 3749.9919 | 3674.4486 | 3438.8237 | -75.5433 | 3730.1852 | 3498.931 | 2994.9168 | 3187.3601 | -542.8251
2.2.1 | Fuel 1 - Domestic Coal | kcal/kg | 3718.6849 | 3765.4308 | 3759.5634 | 46.7459 | 3730.1852 | 3702.9376 | 3700.3483 | -27.2475 | 3730.1852 | 3645.0667 | 3714 | 3645.0667 | -85.1185
2.2.2 | Fuel 2 - Imported Coal | kcal/kg | 4271.2231 | 4400.7725 | 4400.7725 | 129.5495 | 4390.4098 | 4009 | 4009 | -381.4098 | 0 | 4287 | 4287 | 4287 | 4287
2.2.3 | Fuel 3 - Raw Coal |  | 3451.9836 | 3537.3384 | 3293.1886 | 85.3547 | 0 | 3634.6062 | 3219.5414 | 3634.6062 | 0 | 3454.4605 | 2966.121 | 3131.4243 | 3131.4243
2.2.4 | Fuel 4 - Addnl. Raw coal
2.2.5 | LDO | kcal/kg | 10812.2347 | 10813.8187 | 10813.8187 | 1.584 | 10810.3333 | 10764.6911 | 10764.6911 | -45.6422 | 10810.3333 | 10704.6515 | 10690.3631 | 10696.3729 | -113.9605
2.3 | GCV loss in transit |  | 71.0122 | 129.2833 | 235.9275 | 58.2711 | 71.0122 | 170.8437 | 406.4687 | 99.8315 | 16.7317 | 244.4335 | 692.8028 | 521.6059 | 504.8743
2.3.1 | Fuel 1 - Domestic Coal |  | 14.7335 | 0 | 5.8674 | -14.7335 | 16.7317 | 0 | 2.5893 | -16.7317 | 16.7317 | -7.6039 | 0 | -7.6039 | -24.3356
2.3.2 | Fuel 2 - Imported Coal |  | 0 | 13.879 | 13.879 | 13.879 | 0 | 39 | 39 | 39 | 0 | 204 | 204 | 204 | 204
2.3.3 | Fuel 3 - Raw Coal |  | 300 | 300 | 544.1497 | 0 | 0 | 300 | 715.0648 | 300 | 0 | 300 | 703.6964 | 567.0448 | 567.0448
2.3.4 | Fuel 4 - Addnl. Raw coal
2.3.5 | LDO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | Calorific Value (As Fired) | kcal/kg | 3659.5345 | 3555.2741 | 3555.2741 | -104.2604 | 3774.4239 | 3423.0846 | 3423.0846 | -351.3393 | 3766.3333 | 3102.9536 | 2832.4563 | 2935.7379 | -830.5954
2.5.1 | Fuel 1 - Domestic Coal | kcal/kg | 3733.8455 | 3712.5557 | 3712.5557 | -21.2899 | 3766.3333 | 3675.4867 | 3675.4867 | -90.8466 | 3766.3333 | 3788.7977 | 3669.7615 | 3788.7977 | 22.4644
2.5.2 | Fuel 2 - Imported Coal | kcal/kg | 4036.0178 | 3962.9335 | 3962.9335 | -73.0843 | 4036.0178 | 3969.5007 | 3969.5007 | -66.5171 | 0 | 4095 | 4095 | 4095 | 4095
2.5.3 | Fuel 3 - Raw Coal |  | 3216.6551 | 3276.6115 | 3276.6115 | 59.9564 | 0 | 3211.6781 | 3211.6781 | 3211.6781 | 0 | 2937.6128 | 2804.3189 | 2849.4389 | 2849.4389
2.5.4 | Fuel 4 - Addnl. Raw coal
2.5.5 | LDO | kcal/kg | 10812.2347 | 10813.8187 | 10813.8187 | 1.584 | 10810.3333 | 10764.6911 | 10764.6911 | -45.6422 | 10810.3333 | 10704.6515 | 10690.3631 | 10696.3729 | -113.9605
2.6 | Actual stacking loss | kcal/kg | 60.7562 | 120 | 78.2377 | 59.2438 | -24.432 | 120 | 15.739 | 144.432 | -36.1482 | 120 | 120 | 120 | 156.1482
2.6.1 | Fuel 1 - Domestic Coal | kcal/kg | -15.1606 | 52.8751 | 47.0077 | 68.0357 | -36.1482 | 27.4509 | 24.8616 | 63.5991 | -36.1482 | -143.731 | 44.2385 | -143.731 | -107.5829
2.6.2 | Fuel 2 - Imported Coal | kcal/kg | 235.2053 | 437.8391 | 437.8391 | 202.6338 | 354.392 | 39.4993 | 39.4993 | -314.8927 | 0 | 192 | 192 | 192 | 192
2.6.3 | Fuel 3 - Raw Coal |  | 235.3286 | 260.7269 | 16.5771 | 25.3983 | 0 | 422.9281 | 7.8633 | 422.9281 | 0 | 516.8477 | 161.8021 | 281.9854 | 281.9854
2.6.4 | Fuel 4 - Addnl. Raw coal
2.6.5 | LDO | kcal/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7 | Landed Fuel Price per unit | Rs/MT | 6006.1378 | 6222.3511 | 6233.3421 | 216.2133 | 5588.173 | 5110.4242 | 5122.7573 | -477.7489 | 5434.19 | 5019.1419 | 4944.628 | 4973.079 | -461.111
2.7.1 | Fuel 1 - Domestic Coal | Rs/MT | 5262.7555 | 5458.7451 | 5458.7451 | 195.9896 | 5353.8818 | 5269.8697 | 5256.0816 | -84.0121 | 5434.19 | 5369.3308 | 5553.2557 | 5369.3308 | -64.8592
2.7.2 | Fuel 2 - Imported Coal | Rs/MT | 13516.4735 | 14426.0369 | 14514.63 | 909.5634 | 13163.5898 | 7668.8193 | 7662.3268 | -5494.7705 | 13163.5898 | 9268.4143 | 9268.4143 | 9268.4143 | -3895.1755
2.7.3 | Fuel 3 - Raw Coal |  | 4831.6894 | 4871.0883 | 4873.3791 | 39.3989 | 0 | 4847.2617 | 4879.2643 | 4847.2617 | 0 | 4874.7473 | 4848.2666 | 4857.2303 | 4857.2303
2.7.4 | Fuel 4 - Addnl. Raw coal
2.7.5 | LDO | Rs/KL | 69368.3562 | 66271.8 | 66271.8 | -3096.5562 | 73185.1875 | 73853.5048 | 73853.5048 | 668.3173 | 73185.1875 | 73497.5562 | 73240.2722 | 73348.4873 | 163.2998
3 | Fuel Consumption and Heat Contribution (for each fuel separately)
3.1 | Specific Fuel Consumption | kg/kWh | 0.66271 | 0.66992 | 0.63686 | 0.0072085 | 0.64254 | 0.68231 | 0.66324 | 0.039771 | 0.64392 | 0.71776 | 0.8436 | 0.79067 | 0.14675
3.1.1 | Fuel 1 - Domestic Coal | kg/kWh | 0.46183 | 0.30899 | 0.29374 | -0.15284 | 0.62327 | 0.2741 | 0.26644 | -0.34916 | 0.64392 | 0.12675 | 0 | 0.053312 | -0.59061
3.1.2 | Fuel 2 - Imported Coal | kg/kWh | 0.066696 | 0.075737 | 0.071999 | 0.0090403 | 0.019276 | 0.022584 | 0.021953 | 0.0033075 | 0 | 0.0093208 | 0.018391 | 0.014576 | 0.014576
3.1.3 | Fuel 3 - Raw Coal |  | 0.13419 | 0.2852 | 0.27112 | 0.15101 | 0 | 0.38563 | 0.37485 | 0.38563 | 0 | 0.58169 | 0.82521 | 0.72278 | 0.72278
3.1.4 | Fuel 4 - Addnl. Raw coal
3.1.5 | LDO | ml/kWh | 0.5 | 0.5 | 0.081 | 0 | 0.5 | 0.5 | 0.081 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0
3.2 | Total Fuel Consumption | MT | 2246968.0089 | 2339789.0853 | 2223978.171 | 92821.0764 | 2621569.2848 | 2202237.8161 | 2160930.816 | -419331.4688 | 2623337.1982 | 994168.7924 | 1609586.8917 | 2603755.684 | -19581.5142
3.2.1 | Fuel 1 - Domestic Coal | MT | 1565858.1242 | 1079187.7059 | 1025771.902 | -486670.4184 | 2542922.2063 | 884693.7012 | 868099.652 | -1658228.5051 | 2623337.1982 | 175560.6392 | 0 | 175560.6392 | -2447776.5591
3.2.2 | Fuel 2 - Imported Coal | MT | 226138.0085 | 264520.3173 | 251427.539 | 38382.3088 | 78647.0785 | 72891.5239 | 71524.31 | -5755.5546 | 0 | 12910.2132 | 35089.7868 | 48000 | 48000
3.2.3 | Fuel 3 - Raw Coal |  | 454971.8762 | 996081.0621 | 946778.73 | 541109.1859 | 0 | 1244652.5909 | 1221306.854 | 1244652.5909 | 0 | 805697.94 | 1574497.1049 | 2380195.0449 | 2380195.0449
3.2.4 | Fuel 4 - Addnl. Raw coal
3.2.5 | LDO | KL | 1698.5552 | 1746.3144 | 282.621 | 47.7592 | 2040 | 1613.8048 | 568.06 | -426.1952 | 2037 | 692.547 | 954 | 1646.547 | -390.453
3.3 | Heat Content (each fuel separately) | Million kcal | 2425.2231 | 2425.2224 | 2264.226 | -0.00069981 | 2425.2239 | 2425.2441 | 2270.3354 | 0.020165 | 2425.2239 | 2425.2706 | 2425.2769 | 2425.2743 | 0.050348
3.3.1 | Fuel 1 - Domestic Coal | Million kcal | 1724.3988 | 1168.0777 | 1090.5358 | -556.3211 | 2347.4247 | 1046.1197 | 979.3005 | -1301.3049 | 2425.2239 | 522.9418 | 0 | 211.0435 | -2214.1805
3.3.2 | Fuel 2 - Imported Coal | Million kcal | 269.1879 | 305.6171 | 285.3289 | 36.4291 | 77.7993 | 93.0865 | 87.1407 | 15.2872 | 0 | 41.5635 | 76.4396 | 62.3647 | 62.3647
3.3.3 | Fuel 3 - Raw Coal |  | 431.6363 | 951.5276 | 888.3613 | 519.8913 | 0 | 1286.0379 | 1203.8942 | 1286.0379 | 0 | 1860.7653 | 2348.8374 | 2151.8662 | 2151.8662
3.3.4 | Fuel 4 - Addnl. Raw coal
3.3.5 | LDO | Million kcal | 4.7769 | 4.7776 | 0.77397 | 0.00069981 | 4.7761 | 4.7559 | 1.6646 | -0.020165 | 4.7761 | 4.7294 | 4.7231 | 4.7257 | -0.050348
| Total Heat Content | Million kcal | 2430 | 2430 | 2265 | 0 | 2430 | 2430 | 2272 | 0 | 2430 | 2430 | 2430 | 2430 | 0
4 | Total Fuel Cost
4.1.1 | Fuel 1 - Domestic Coal | Rs Crore | 824.0728 | 589.1011 | 559.9427 | -234.9718 | 1361.4505 | 466.2221 | 456.2803 | -895.2284 | 1425.5713 | 94.2643 | 0 | 94.2643 | -1331.307
4.1.2 | Fuel 2 - Imported Coal | Rs Crore | 305.6588 | 381.598 | 364.9378 | 75.9391 | 103.5278 | 55.8992 | 54.8043 | -47.6286 | 0 | 11.9657 | 32.5227 | 44.4884 | 44.4884
4.1.3 | Fuel 3 - Raw Coal |  | 219.8283 | 485.1999 | 461.4012 | 265.3716 | 0 | 603.3157 | 595.9079 | 603.3157 | 0 | 392.7574 | 763.3582 | 1156.1156 | 1156.1156
4.1.4 | Fuel 4 - Addnl. Raw coal
4.1.5 | LDO | Rs Crore | 11.7826 | 11.5731 | 1.873 | -0.20946 | 14.9298 | 11.9185 | 4.1953 | -3.0113 | 14.9078 | 5.0901 | 6.9871 | 12.0772 | -2.8306
| Total Fuel Cost | Rs Crore | 1361.3426 | 1467.4721 | 1388.1546 | 106.1295 | 1479.9081 | 1137.3554 | 1111.1877 | -342.5526 | 1440.4791 | 504.0775 | 802.868 | 1306.9454 | -133.5337
5 | Other Charges and Adjustments
5.1.1 | Other Charges (pl. specify details) | Rs Crore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1.2 | Other Adjustments (pl. specify details)- PLF incentive | Rs Crore | 0 | 2.3816 | 0 | 2.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Other Charges and Adjustments | Rs Crore | 0 | 2.3816 | 0 | 2.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Total Cost (4+5) | Rs Crore | 1361.3426 | 1469.8536 | 1388.1546 | 108.5111 | 1479.9081 | 1137.3554 | 1111.1877 | -342.5526 | 1440.4791 | 504.0775 | 802.868 | 1306.9454 | -133.5337
7 | Energy Charge per unit (ex-bus) (6/1.11) | Rs/kWh | 4.4378 | 4.6605 | 4.4015 | 0.22269 | 4.0169 | 3.9024 | 3.8126 | -0.1145 | 3.9156 | 4.0302 | 4.6599 | 4.3951 | 0.47947
| DISCOM Scheduled generation |  | 3157.7861 | 1469.3064 | 1389.8899 |  | 2810.4301 | 1096.7313 | 1071.4983
* - In case MTR Order is yet to be issued, then MYT Order values to be captured under this column | [10 empty] | 1463.379 | 1542.2171 | 2147.8641 | 1865.543
|  |  | 69.69% | 46.12% | 46.12% |  | 97% | 40.17% | 40.17% |  | 100% | 17.66% | 0% | 6.743%
Note |  |  | 10.06% | 11.31% | 11.31% |  | 3% | 3.31% | 3.31% |  | 0% | 1.299% | 2.18% | 1.843%
1 | Details to be submitted for each primary and secondary fuel separately |  | 20.25% | 42.57% | 42.57% |  | 0% | 56.52% | 56.52% |  | 0% | 81.04% | 97.82% | 91.41%
2 | The energy charge should be computed for open cycle operation and combined cycle operation separately in case of gas/liquid fuel fired plants.
3 | Operational data are to be submitted for each Unit of each station separately
Note on N20: ANUPAM PATRA: Actual till Aug 24
Note on N30: ANUPAM PATRA: Actual net generation till Aug 24